## Sayfa1
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 1984.4505
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 2078.3955
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 4062.846
f(Hz) | 50 | N1 | 1794 | Efficiency(%) | 99.194
Temp Min(Celc) | -30 | AreaCopperIn(m2) | 0.012257
Temp Max(Celc) | 50 | AreaCopperOut(m2) | 0.012257
FF | 0.3 | Window Area(m2) | 0.08171
J(A/mm2) | 3 | Window Edge(m) | 0.28585
N2 | 1300
Core Specs |  | Core Dependent Calculations
B(T) | 1.5 | Area(m2) | 0.05775
Relative Perm | 610 | Edge(m) | 0.24031
CoreLoss(W/kg) | 2.25 | H(A/m) | 1956.8231
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.76647
Density(kg/dm3) | 7.6 | Middle Length(m) | 2.1046
|  | One Turn Length(m) | 0.96125
|  | Core Mass(kg) | 923.7313
Winding Specs |  | Winding Calculations
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 4.724
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 2.4806
Temperature Coeff | 0.0038 | Copper Mass(kg) | 142550.5741