## Sayfa1
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 1173.6473
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 11536.3658
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 12710.0131
f(Hz) | 50 | N1 | 345 | Efficiency(%) | 97.521
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 1666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 1666.6667
FF | 0.3 | Window Area(m2) | 0.011111
J(A/mm2) | 3 | Window Edge(m) | 0.10541
N2 | 250
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.37538 | Reluctance | 12846.468
Relative Perm | 474 | Edge(m) | 0.61268 | Mutual Inductance(H) | 9.2652
CoreLoss(W/kg) | 1.363 | H(A/m) | 2014.6195 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 1.3308 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.8724
Core Cost ($/kg) | 3 | One Turn Length(m) | 2.0904
|  | Core Mass(kg) | 8463.9514
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 2.7939 | Material Cost | 25890.197
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 1.4671 | Energy Lost (0.07$/kwh) | 155875.6007
Temperature Coeff | 0.0038 | Copper Mass(kg) | 62.2928
Winding Cost ($/kg) | 8