## Single Design
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2905.0781
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 2077.086
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 4982.1641
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 99.0134
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667
FF | 0.3 | Window Area(m2) | 0.044444
J(A/mm2) | 3 | Window Edge(m) | 0.21082
N2 | 1000
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.093844 | Reluctance | 18368.0969
Relative Perm | 955 | Edge(m) | 0.30634 | Mutual Inductance(H) | 103.6798
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.8235 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.0686
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.2935
|  | Core Mass(kg) | 1523.9076
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.9155 | Material Cost | 5805.2488
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.6313 | Energy Lost (0.07$/kwh) | 61101.2606
Temperature Coeff | 0.0038 | Copper Mass(kg) | 154.1908
Winding Cost ($/kg) | 8

## Turn Number changes
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 1173.6473
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 11536.3658
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 12710.0131
f(Hz) | 50 | N1 | 345 | Efficiency(%) | 97.521
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 1666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 1666.6667
FF | 0.3 | Window Area(m2) | 0.011111
J(A/mm2) | 3 | Window Edge(m) | 0.10541
N2 | 250
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.37538 | Reluctance | 6376.1527
Relative Perm | 955 | Edge(m) | 0.61268 | Mutual Inductance(H) | 18.6672
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 1.3308 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.8724
Core Cost ($/kg) | 3 | One Turn Length(m) | 2.0904
|  | Core Mass(kg) | 8463.9514
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 2.7939 | Material Cost | 25890.197
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 1.4671 | Energy Lost (0.07$/kwh) | 155875.6007
Temperature Coeff | 0.0038 | Copper Mass(kg) | 62.2928
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 1555.1141
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 6202.2297
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 7757.3438
f(Hz) | 50 | N1 | 552 | Efficiency(%) | 98.4722
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 2666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 2666.6667
FF | 0.3 | Window Area(m2) | 0.017778
J(A/mm2) | 3 | Window Edge(m) | 0.13333
N2 | 400
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.23461 | Reluctance | 8775.6138
Relative Perm | 955 | Edge(m) | 0.48437 | Mutual Inductance(H) | 34.7217
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 1.1021 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.4708
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.7311
|  | Core Mass(kg) | 4550.4253
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 3.7019 | Material Cost | 14311.5933
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 1.9439 | Energy Lost (0.07$/kwh) | 95136.0643
Temperature Coeff | 0.0038 | Copper Mass(kg) | 82.5397
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 1906.2656
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 4158.1261
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 6064.3917
f(Hz) | 50 | N1 | 759 | Efficiency(%) | 98.8017
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 3666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 3666.6667
FF | 0.3 | Window Area(m2) | 0.024444
J(A/mm2) | 3 | Window Edge(m) | 0.15635
N2 | 550
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.17063 | Reluctance | 11123.2758
Relative Perm | 955 | Edge(m) | 0.41307 | Mutual Inductance(H) | 51.7906
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.98248 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.2777
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.5433
|  | Core Mass(kg) | 3050.7161
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 4.5379 | Material Cost | 9961.5683
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 2.3828 | Energy Lost (0.07$/kwh) | 74373.6993
Temperature Coeff | 0.0038 | Copper Mass(kg) | 101.1775
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2243.8927
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 3112.8362
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 5356.7288
f(Hz) | 50 | N1 | 966 | Efficiency(%) | 98.94
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 4666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 4666.6667
FF | 0.3 | Window Area(m2) | 0.031111
J(A/mm2) | 3 | Window Edge(m) | 0.17638
N2 | 700
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.13406 | Reluctance | 13488.4491
Relative Perm | 955 | Edge(m) | 0.36615 | Mutual Inductance(H) | 69.1819
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.90867 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.1701
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.4273
|  | Core Mass(kg) | 2283.8123
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 5.3416 | Material Cost | 7804.2168
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 2.8049 | Energy Lost (0.07$/kwh) | 65694.9223
Temperature Coeff | 0.0038 | Copper Mass(kg) | 119.0975
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2575.4995
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 2488.4195
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 5063.9189
f(Hz) | 50 | N1 | 1173 | Efficiency(%) | 98.9974
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 5666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 5666.6667
FF | 0.3 | Window Area(m2) | 0.037778
J(A/mm2) | 3 | Window Edge(m) | 0.19437
N2 | 850
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.1104 | Reluctance | 15899.0478
Relative Perm | 955 | Edge(m) | 0.33227 | Mutual Inductance(H) | 86.5416
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.85891 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.1065
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.3492
|  | Core Mass(kg) | 1825.6929
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.131 | Material Cost | 6570.6624
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.2194 | Energy Lost (0.07$/kwh) | 62103.9016
Temperature Coeff | 0.0038 | Copper Mass(kg) | 136.6979
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2905.0781
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 2077.086
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 4982.1641
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 99.0134
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667
FF | 0.3 | Window Area(m2) | 0.044444
J(A/mm2) | 3 | Window Edge(m) | 0.21082
N2 | 1000
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.093844 | Reluctance | 18368.0969
Relative Perm | 955 | Edge(m) | 0.30634 | Mutual Inductance(H) | 103.6798
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.8235 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.0686
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.2935
|  | Core Mass(kg) | 1523.9076
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.9155 | Material Cost | 5805.2488
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.6313 | Energy Lost (0.07$/kwh) | 61101.2606
Temperature Coeff | 0.0038 | Copper Mass(kg) | 154.1908
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 3234.9804
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 1787.242
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 5022.2224
f(Hz) | 50 | N1 | 1587 | Efficiency(%) | 99.0055
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 7666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 7666.6667
FF | 0.3 | Window Area(m2) | 0.051111
J(A/mm2) | 3 | Window Edge(m) | 0.22608
N2 | 1150
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.081603 | Reluctance | 20902.0425
Relative Perm | 955 | Edge(m) | 0.28566 | Mutual Inductance(H) | 120.4939
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.7974 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.047
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.2526
|  | Core Mass(kg) | 1311.2561
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 7.7009 | Material Cost | 5307.3742
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 4.0437 | Energy Lost (0.07$/kwh) | 61592.5357
Temperature Coeff | 0.0038 | Copper Mass(kg) | 171.7007
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 3566.687
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 1572.7014
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 5139.3884
f(Hz) | 50 | N1 | 1794 | Efficiency(%) | 98.9826
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 8666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 8666.6667
FF | 0.3 | Window Area(m2) | 0.057778
J(A/mm2) | 3 | Window Edge(m) | 0.24037
N2 | 1300
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.072188 | Reluctance | 23504.0476
Relative Perm | 955 | Edge(m) | 0.26868 | Mutual Inductance(H) | 136.9311
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.77772 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.0362
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.2216
|  | Core Mass(kg) | 1153.8528
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 8.4905 | Material Cost | 4976.0106
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 4.4584 | Energy Lost (0.07$/kwh) | 63029.4596
Temperature Coeff | 0.0038 | Copper Mass(kg) | 189.3065
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 3901.1733
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 1407.8272
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 5309.0005
f(Hz) | 50 | N1 | 2001 | Efficiency(%) | 98.9494
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 9666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 9666.6667
FF | 0.3 | Window Area(m2) | 0.064444
J(A/mm2) | 3 | Window Edge(m) | 0.25386
N2 | 1450
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.06472 | Reluctance | 26175.5026
Relative Perm | 955 | Edge(m) | 0.2544 | Mutual Inductance(H) | 152.9675
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.76266 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.033
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.198
|  | Core Mass(kg) | 1032.8886
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 9.2867 | Material Cost | 4755.1443
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 4.8765 | Energy Lost (0.07$/kwh) | 65109.5826
Temperature Coeff | 0.0038 | Copper Mass(kg) | 207.0598
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 4239.1025
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 1277.3222
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 5516.4247
f(Hz) | 50 | N1 | 2208 | Efficiency(%) | 98.9088
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 10666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 10666.6667
FF | 0.3 | Window Area(m2) | 0.071111
J(A/mm2) | 3 | Window Edge(m) | 0.26667
N2 | 1600
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.058652 | Reluctance | 28916.7904
Relative Perm | 955 | Edge(m) | 0.24218 | Mutual Inductance(H) | 168.5963
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.75103 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.0354
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.1797
|  | Core Mass(kg) | 937.1402
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 10.0912 | Material Cost | 4611.3873
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 5.2989 | Energy Lost (0.07$/kwh) | 67653.4324
Temperature Coeff | 0.0038 | Copper Mass(kg) | 224.9958
Winding Cost ($/kg) | 8

## Core Changes
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2905.0781
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 2077.086
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 4982.1641 | Steel |  | M700-35A
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 99.0134 | B(T) | 1.2 | B(T) | 1.63
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667 |  |  | Relative Perm | 955 | Relative Perm | 518
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667 |  |  | CoreLoss(W/kg) | 1.363 | CoreLoss(W/kg) | 7.1867
FF | 0.3 | Window Area(m2) | 0.044444 |  |  | Lamination Thickness(m) | 0.00035 | Lamination Thickness(m) | 0.00035
J(A/mm2) | 3 | Window Edge(m) | 0.21082 |  |  | Density(kg/dm3) | 7.85 | Density(kg/dm3) | 7.8
N2 | 1000 |  |  |  |  | Core Cost ($/kg) | 3 | Core Cost ($/kg) | 3
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.2 | Area(m2) | 0.093844 | Reluctance | 18368.0969
Relative Perm | 955 | Edge(m) | 0.30634 | Mutual Inductance(H) | 103.6798
CoreLoss(W/kg) | 1.363 | H(A/m) | 999.9263 | Leakage Ind 1 (H) | 0.15155 | M235-35A |  | M940-50A
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.8235 | Leakage Ind 2 (H) | 0.079577 | B(T) | 1.53 | B(T) | 1.65
Density(kg/dm3) | 7.85 | Middle Length(m) | 2.0686 |  |  | Relative Perm | 487 | Relative Perm | 525
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.2935 |  |  | CoreLoss(W/kg) | 2.295 | CoreLoss(W/kg) | 8.305
|  | Core Mass(kg) | 1523.9076 |  |  | Lamination Thickness(m) | 0.00035 | Lamination Thickness(m) | 0.005
[6 empty] | Density(kg/dm3) | 7.6 | Density(kg/dm3) | 7.85
Winding Specs |  | Winding Calculations |  | Costs |  | Core Cost ($/kg) | 3 | Core Cost ($/kg) | 0.21
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.9155 | Material Cost | 5805.2488
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.6313 | Energy Lost (0.07$/kwh) | 61101.2606
Temperature Coeff | 0.0038 | Copper Mass(kg) | 154.1908 |  |  | M250-50A |  | M1000-65A
Winding Cost ($/kg) | 8 |  |  |  |  | B(T) | 1.55 | B(T) | 1.66
[6 empty] | Relative Perm | 493 | Relative Perm | 528
Design Inputs |  | Initial Calculations |  | Losses |  | CoreLoss(W/kg) | 2.4593 | CoreLoss(W/kg) | 8.7427
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2657.8499 | Lamination Thickness(m) | 0.005 | Lamination Thickness(m) | 0.0065
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 2475.7373 | Density(kg/dm3) | 7.6 | Density(kg/dm3) | 7.8
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 5133.5872 | Core Cost ($/kg) | 0.21 | Core Cost ($/kg) | 0.16154
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 98.9837
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667 |  |  | M310-65A |  | M1000-100A
FF | 0.3 | Window Area(m2) | 0.044444 |  |  | B(T) | 1.56 | B(T) | 1.65
J(A/mm2) | 3 | Window Edge(m) | 0.21082 |  |  | Relative Perm | 496 | Relative Perm | 525
N2 | 1000 |  |  |  |  | CoreLoss(W/kg) | 3.016 | CoreLoss(W/kg) | 9.779
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations |  | Lamination Thickness(m) | 0.0065 | Lamination Thickness(m) | 0.01
B(T) | 1.53 | Area(m2) | 0.073603 | Reluctance | 42813.255 | Density(kg/dm3) | 7.6 | Density(kg/dm3) | 7.8
Relative Perm | 487 | Edge(m) | 0.2713 | Mutual Inductance(H) | 44.4816 | Core Cost ($/kg) | 0.16154 | Core Cost ($/kg) | 0.105
CoreLoss(W/kg) | 2.295 | H(A/m) | 2500.0725 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.75342 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.6 | Middle Length(m) | 1.9285
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.1835 |  |  | M600-100A
|  | Core Mass(kg) | 1078.7526 |  |  | B(T) | 1.59
[6 empty] | Relative Perm | 506
Winding Specs |  | Winding Calculations |  | Costs |  | CoreLoss(W/kg) | 9.4234
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.327 | Material Cost | 4364.8084 | Lamination Thickness(m) | 0.01
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.3223 | Energy Lost (0.07$/kwh) | 62958.3133 | Density(kg/dm3) | 7.6
Temperature Coeff | 0.0038 | Copper Mass(kg) | 141.0688 |  |  | Core Cost ($/kg) | 0.105
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2645.4605
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 2609.2416
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 5254.7021
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 98.96
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667
FF | 0.3 | Window Area(m2) | 0.044444
J(A/mm2) | 3 | Window Edge(m) | 0.21082
N2 | 1000
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.55 | Area(m2) | 0.072653 | Reluctance | 42688.9876
Relative Perm | 493 | Edge(m) | 0.26954 | Mutual Inductance(H) | 44.611
CoreLoss(W/kg) | 2.4593 | H(A/m) | 2501.9286 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.005 | OuterEdge(m) | 0.7499 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.6 | Middle Length(m) | 1.9214
Core Cost ($/kg) | 0.21 | One Turn Length(m) | 1.1779
|  | Core Mass(kg) | 1060.9549
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.2975 | Material Cost | 1346.0903
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.3068 | Energy Lost (0.07$/kwh) | 64443.6669
Temperature Coeff | 0.0038 | Copper Mass(kg) | 140.4112
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2639.3554
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 3173.6009
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 5812.9562
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 98.8508
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667
FF | 0.3 | Window Area(m2) | 0.044444
J(A/mm2) | 3 | Window Edge(m) | 0.21082
N2 | 1000
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.56 | Area(m2) | 0.072188 | Reluctance | 42627.6085
Relative Perm | 496 | Edge(m) | 0.26868 | Mutual Inductance(H) | 44.6753
CoreLoss(W/kg) | 3.016 | H(A/m) | 2502.8398 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.0065 | OuterEdge(m) | 0.74817 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.6 | Middle Length(m) | 1.918
Core Cost ($/kg) | 0.16154 | One Turn Length(m) | 1.1752
|  | Core Mass(kg) | 1052.2549
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.283 | Material Cost | 1290.6771
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.2992 | Energy Lost (0.07$/kwh) | 71290.0954
Temperature Coeff | 0.0038 | Copper Mass(kg) | 140.0872
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2621.3868
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 9677.0557
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 12298.4425
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 97.5994
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667
FF | 0.3 | Window Area(m2) | 0.044444
J(A/mm2) | 3 | Window Edge(m) | 0.21082
N2 | 1000
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.59 | Area(m2) | 0.070826 | Reluctance | 42362.5235
Relative Perm | 506 | Edge(m) | 0.26613 | Mutual Inductance(H) | 44.9548
CoreLoss(W/kg) | 9.4234 | H(A/m) | 2500.5569 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.01 | OuterEdge(m) | 0.74308 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.6 | Middle Length(m) | 1.9078
Core Cost ($/kg) | 0.105 | One Turn Length(m) | 1.1672
|  | Core Mass(kg) | 1026.9176
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.2402 | Material Cost | 1220.8942
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.2767 | Energy Lost (0.07$/kwh) | 150828.0986
Temperature Coeff | 0.0038 | Copper Mass(kg) | 139.1335
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2598.2047
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 7337.5564
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 9935.7611
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 98.0516
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667
FF | 0.3 | Window Area(m2) | 0.044444
J(A/mm2) | 3 | Window Edge(m) | 0.21082
N2 | 1000
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.63 | Area(m2) | 0.069087 | Reluctance | 42129.9423
Relative Perm | 518 | Edge(m) | 0.26284 | Mutual Inductance(H) | 45.203
CoreLoss(W/kg) | 7.1867 | H(A/m) | 2504.0787 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.00035 | OuterEdge(m) | 0.73651 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.8 | Middle Length(m) | 1.8947
Core Cost ($/kg) | 3 | One Turn Length(m) | 1.1569
|  | Core Mass(kg) | 1020.9958
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.185 | Material Cost | 4166.2118
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.2478 | Energy Lost (0.07$/kwh) | 121852.1739
Temperature Coeff | 0.0038 | Copper Mass(kg) | 137.9031
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2586.9311
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 8401.8471
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 10988.7782
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 97.8495
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667
FF | 0.3 | Window Area(m2) | 0.044444
J(A/mm2) | 3 | Window Edge(m) | 0.21082
N2 | 1000
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.65 | Area(m2) | 0.06825 | Reluctance | 41936.3023
Relative Perm | 525 | Edge(m) | 0.26125 | Mutual Inductance(H) | 45.4117
CoreLoss(W/kg) | 8.305 | H(A/m) | 2501.0062 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.005 | OuterEdge(m) | 0.73331 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.85 | Middle Length(m) | 1.8883
Core Cost ($/kg) | 0.21 | One Turn Length(m) | 1.1519
|  | Core Mass(kg) | 1011.6613
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.1582 | Material Cost | 1310.8864
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.2337 | Energy Lost (0.07$/kwh) | 134766.3759
Temperature Coeff | 0.0038 | Copper Mass(kg) | 137.3047
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2581.3708
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 8720.758
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 11302.1288
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 97.7895
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667
FF | 0.3 | Window Area(m2) | 0.044444
J(A/mm2) | 3 | Window Edge(m) | 0.21082
N2 | 1000
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.66 | Area(m2) | 0.067839 | Reluctance | 41880.7096
Relative Perm | 528 | Edge(m) | 0.26046 | Mutual Inductance(H) | 45.472
CoreLoss(W/kg) | 8.7427 | H(A/m) | 2501.8675 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.0065 | OuterEdge(m) | 0.73174 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.8 | Middle Length(m) | 1.8851
Core Cost ($/kg) | 0.16154 | One Turn Length(m) | 1.1494
|  | Core Mass(kg) | 997.494
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.145 | Material Cost | 1257.2103
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.2267 | Energy Lost (0.07$/kwh) | 138609.3075
Temperature Coeff | 0.0038 | Copper Mass(kg) | 137.0096
Winding Cost ($/kg) | 8
Design Inputs |  | Initial Calculations |  | Losses
S(VA) | 500000 | N1/N2 | 1.38 | Copper Loss(W) | 2586.9311
Vin(Vrms) | 34500 | CurrIn(Arms) | 14.4928 | Core Loss(W) | 9830.0229
Vo(Vrms) | 25000 | CurrOut(Arms) | 20 | Total Loss(W) | 12416.954
f(Hz) | 50 | N1 | 1380 | Efficiency(%) | 97.5768
Temp Min(Celc) | -30 | N1*AreaCopperIn(mm2) | 6666.6667
Temp Max(Celc) | 50 | N2*AreaCopperOut(mm2) | 6666.6667
FF | 0.3 | Window Area(m2) | 0.044444
J(A/mm2) | 3 | Window Edge(m) | 0.21082
N2 | 1000
Core Specs |  | Core Dependent Calculations |  | Inductance Calculations
B(T) | 1.65 | Area(m2) | 0.06825 | Reluctance | 41936.3023
Relative Perm | 525 | Edge(m) | 0.26125 | Mutual Inductance(H) | 45.4117
CoreLoss(W/kg) | 9.779 | H(A/m) | 2501.0062 | Leakage Ind 1 (H) | 0.15155
Lamination Thickness(m) | 0.01 | OuterEdge(m) | 0.73331 | Leakage Ind 2 (H) | 0.079577
Density(kg/dm3) | 7.8 | Middle Length(m) | 1.8883
Core Cost ($/kg) | 0.105 | One Turn Length(m) | 1.1519
|  | Core Mass(kg) | 1005.2176
Winding Specs |  | Winding Calculations |  | Costs
Density(kg/m3) | 8940 | Input Wind. Resist @50C | 6.1582 | Material Cost | 1203.9854
Resistivity(ohm-m) @20C | 1.68e-08 | Output Wind. Resist @50C | 3.2337 | Energy Lost (0.07$/kwh) | 152281.5238
Temperature Coeff | 0.0038 | Copper Mass(kg) | 137.3047
Winding Cost ($/kg) | 8